Agenda Item:  	D.2

Request for Decision

| Title | Odour Management Project Update |
| --- | --- |
| Proposed Motion | That Council approve up to $80,000 of additional funding from the Utility Capital Reserve towards the Odour Management Project. |
| Administrative Recommendation | Administration recommends that Council approve up to $80,000 of additional funding from Utility Capital Reserves to complete aspects of the Odour Management Project that will mitigate excessive hydrogen sulphide odour and corrosion issues in Sturgeon Valley and Cardiff. |
| Previous Council Direction | May 22, 2018 – Motion 155/18: That Council approve funding for a Sturgeon Valley Wastewater Odour Management Study up to $80,000 from Utility Operating Reserve 8.23. |
| Report | Background Information 2017 - In September 2017, the Utility Services Department started receiving odour complaints near the community of River’s Gate. The complaints appeared to correspond with the commissioning of River’s Gate Lift Station. - By December 2017, it was clear that odours were originating from the newly installed River’s Gate Lift Station. Upon further investigation, it was determined that the odour control unit in the lift station could not handle the excessive levels of hydrogen sulphide gas (H2S) going through the collection system. 2018 - In January 2018, Associated Engineering was retained to investigate the source of the odour upstream of the River’s Gate Lift Station. - Associated Engineering conducted a wastewater sampling program in the wet well of the Bellerose and Sturgeon Valley Lift Stations which saw air quality monitoring data in the lift station register H2S in excess of 1800 parts per million (ppm). - On February 28, 2018, Alberta Ministry of Environment and Parks contacted Utility Services indicating that complaints had been reported through the Environmental Reporting Hotline and requested the County to investigate the cause of the odour. They also recommended that testing be conducted. - On March 1, 2018, Utility Services set up two H2S passive air samplers, one directly next to the lift station and the other at the entrance to River’s Gate subdivision. - The results from the H2S passive samplers indicated that there was a presence of H2S at the lift station but results were inconclusive. - On March 20, 2018, it was decided to bypass a portion of the River’s Gate Lift Station to provide temporary relief to residents in the area until a more comprehensive study could be implemented. Complaints dropped as a result. - On May 22, 2018, Council approved and funded an Odour Management Study to understand where odours were developing and what cost-effective solutions Sturgeon County could employ to fix them, as well as provide key recommendation on preventing continued issues. - By mid-August 2018, a report was generated by Associated Engineering identifying that the significant H2S was a direct result of the septic tanks located off low pressure sewer systems (e.g. Sturgeon Valley and Cardiff). - The odour management report highlighted that the Sturgeon Valley Lift Station contained the highest levels of H2S and that chemical dosing would be needed upstream of the lift station to allow appropriate contact time with the wastewater. - The study also explored piloting several odour reducing chemicals, which saw the greatest return on investment with calcium nitrate mixing. The challenge, however, is that calcium nitrate requires a 45-minute contact time with the wastewater to be effective. - Recommendations from Associated Engineering included installing realtime H2S sensors to monitor fluctuations in H2S; a chemical dosing shed upstream of the Sturgeon Valley Lift Station to house the vast amount of chemicals needed to reduce sewer odours; and upgrades to the underground infrastructure. 2019 - Injecting calcium nitrate over this past summer saw a significant reduction of corrosive gas, with results indicating a decrease in H2S formation from 1800 ppm to 20 ppm. - Allin Ridge Water Reservoir was identified as an opportunistic chemical dosing site since the sump from the reservoir is the furthest upstream (County-owned) connection to the low-pressure system. Injecting at Allin Ridge Reservoir would be the most cost-effective solution to providing the necessary contact time for the dosing chemicals. - The past summer, while piloting the calcium nitrate solution from Allin Ridge Reservoir, monitoring results showed near zero ppm of H2S gas in the system. - As a result, Utility and Waste Management Services (UWMS) felt that the odour control system was now optimized. However, with complaints returning in September, UWMS raised concerns with Associated Engineering. - Associated Engineering determined that due to all the rain received over the summer, it was very likely that the odour management chemical dosing program was inadvertently aided with all the extra rain flushing. Next Steps – 2019/2020 - Following Associated Engineering’s recommendations, UWMS has purchased the realtime H2S sensors. Vector Electric has been retained to install the sensors at Sturgeon Valley Lift Station, River’s Gate Lift Station, Cardiff Lift Station and a sensor for the River’s Gate subdivision. - UWMS is looking to re-route wastewater from Bellerose Lift Station to mix with Sturgeon Valley Lift Station wastewater. Mixing could assist the calcium nitrate injections by adding fresh gravity sewage to high sulphide containing sewage, requiring fewer chemical additives. - Associated Engineering is providing costs estimates for underground infrastructure hydraulic improvements, which could assist Sturgeon County when further development occurs in the area. - Associated Engineering is prepared to investigate air handling improvements at River’s Gate Lift Station, which could be added as a service enhancement for 2021. - Associated Engineering recommends that the County develop a Sturgeon Valley Community Gravity Sewer Concept Study which would be a strategic sewer servicing document that would align with Sturgeon County’s Offsite Levy Bylaw. - Lastly, the Allin Ridge Chemical Dosing Shed was purchased; however, estimates for shed installation and commissioning exceed budget estimates. - UWMS is investigating alterative options to ensure completion of the initial scope of the odour management project. External Communication - Information has been updated on Sturgeon County’s website regarding recommended septic tank maintenance guidelines. - Agriculture Services performs an annual septic tank workshop to residents wishing to better understand their septic tank. - UWMS has been addressing calls and emails from concerned residents on a regular basis. Relevant Policy/Legislation/Practices: - Bylaw 1408/18 Sanitary Sewer Bylaw - ACRWC Bylaw “Quality of Wastewater” No. 8 - Alberta Environment & Parks’ Alberta Air Quality Objectives (2017) |

| Implication of Administrative Recommendation | Strategic Alignment: Environmental Stewardship - Sturgeon County will continue to comply with provincial and federal environmental regulations and the Alberta Capital Region Wastewater Commission’s (ACRWC’s) bylaw to minimize the air quality impact of Sturgeon County’s sewer system on the environment. Maintain and Enhance Strong Communities – Providing $80,000 of additional funds to support the Odour Management Project would seek to positively improve the impact on residents’ quality of life in Sturgeon Valley and Cardiff. Strong Local Governance and Regional Leadership – Supporting the ongoing learnings of the Odour Management Project will promote fiscal stability and sustainability as the study will provide ways to prevent corrosion related issues within Sturgeon County’s and the ACRWSC’s wastewater infrastructure. Organizational: - Administration is required to prepare an Odour Management Action Plan to the ACRWC on the onset of capital projects. Financial: - 2019 Capital Funding for the Odour Management Project was approved in 2018 for a total amount of $230,000. The projected scope included chemical dosing on each of the County’s each lift stations. Additional recommendations have been developed to further aid in the project delivery. - The current available balance in the Utility Capital Reserve is $1.3 million. Project Cost Breakdown Realtime H2S Sensors (purchased); $44,000. Vector H2S Sensor Installation (booked); $15,000. Chemical Dosing Shed (purchased); $28,000. ClearTech Calcium Nitrate Injection (purchased); $43,000. Contractor Chemical Dosing Shed Install (on hold); $106,000. TOTAL; $236,000. |
| --- | --- |
| Alternatives Considered | Council could decide to have Administration defer installation of the chemical shed to the 2020 capital budget process. As part of the review process, Administration would continue to look at additional cost-saving opportunities. |
| Implications of Alternatives | Strategic Alignment: - None. Organizational: - Administration would continue supporting the optimization of the Odour Management Project. Financial: - Under some circumstances, expenses would need to be shifted to the Utility Operating Budget. |
| Follow up Action | If Council approves the proposed motions, Administration will continue to investigate alternatives to reduce the projected $80,000 requirement to complete the project. |
| Attachment(s) | Sturgeon County Odour Control Project Update Presentation |
| Report Reviewed by: | Manager, Utility & Waste Management Services General Manager, Infrastructure Services Reegan McCullough, County Commissioner – CAO |

Strategic Alignment Checklist

Vision: Sturgeon County: a diverse, active community that pioneers opportunities and promotes initiative while embracing rural lifestyles.

Mission: Provide quality, cost effective services and infrastructure to meet the diverse needs of the Sturgeon County community, while improving competitiveness and sustainability.

| Focus Areas | Not consistent | N/A | Consistent |
| --- | --- | --- | --- |
| Planned Growth and Prosperity |  |  |  |
| We encourage varied and integrated enterprises that enhance our strong economic base, while balancing the needs of the community and natural environment. (Strategic Plan and MDP pg. 36) | ☐ | ☒ | ☐ |
| - Supports a strong thriving business environment to strengthen our economic foundation | ☐ | ☒ | ☐ |
| - Plans for responsible growth through the MDP and regional growth plan. | ☐ | ☒ | ☐ |
| - Manages growth for current and future developments through: - transparent bylaws, policies and processes to enable responsible land development | ☐ | ☒ | ☐ |
| - targeting growth around existing and identified future growth areas | ☐ | ☒ | ☐ |
| Maintain and Enhance Strong Communities |  |  |  |
| We are committed to a safe and viable community, where our residents are provided with access to opportunities and quality of life. (Strategic Plan and pg. 27 MDP) | ☐ | ☐ | ☒ |
| - Provides access to programs and services that have a positive impact on residents’ quality of life | ☐ | ☒ | ☐ |
| - Provides access to safe and reliable infrastructure assets | ☐ | ☐ | ☒ |
| - Supports the safety of people and property | ☐ | ☐ | ☒ |
| Strong Local and Regional Governance |  |  |  |
| We promote consistent and accountable leadership through collaborative and transparent processes (Strategic Plan and pg. 27 MDP) | ☐ | ☒ | ☐ |
| - Provides effective leadership and management consistent with Strategic Plan, MDP, master plans, bylaws, policies, community engagement | ☐ | ☒ | ☐ |
| - Considers fiscal stability and sustainability | ☐ | ☐ | ☒ |
| - Fosters collaborative intergovernmental partnerships | ☐ | ☒ | ☐ |
| Community Identity & Spirit |  |  |  |
| We will build upon our strengths, where together we will create an inclusive, caring community (Strategic Plan and MDP pg. 27) | ☐ | ☒ | ☐ |
| - Promotes and/or enhances residents’ identification with Sturgeon County | ☐ | ☒ | ☐ |
| - Support and/or collaborate with voluntary organizations in the region | ☐ | ☒ | ☐ |
| Environmental Stewardship |  |  |  |
| We foster a healthy environment and minimize our impact on ecosystems. (Strategic Plan and MDP pg. 27) | ☐ | ☐ | ☒ |
| - Plans and partnerships that minimize environmental impact on natural areas | ☐ | ☐ | ☒ |
| - Provides awareness of environmental issues impacting the County | ☐ | ☐ | ☒ |